## Note
NOTE: / Use this spreadsheet, workbook “k-factors”, to calculate k-factor, if you have problem with typing directly into the script. Total calculated “K”, cell “F24” input into main script as user defined k (“User”). Other fitting quantities initiate as “zero” (0). / Column “Sym” in workbook “k-factors” (Column “B”) refer to variable name in script file “dwheadloss.m”. / Column “User's k”, column “E” is here to help user to input his own k-factors for each fitting, if predefined does not fit needs. Total k-factor for a fitting is calculated as ratio between predefined and user's k-factors (k-predefined/user's-K). Or, one can choose to change formula in column “F” (Total K) or add more fittings. / Beware that above manipulation doesn't work with Contraction/Enlargements as k-factor for those are calculated inside script. “numContraction” and “numEnlarg” must be entered inside main script “dwheadloss.m”! “k-factors” for those are not used to calculate “K-factor” - cell “F24”.

## k-factors
	Sym	k factor	Quantity	User's “k”	Total K
Standard 90 deg Elbow	num_90deg_el	0.54	0	1	0
LR Elbow	numLR_el	0.6	0	1	0
SR Elbow	num_SR_el	0.9	0	1	0
Return bend	numRet_Bnd	2.2	0	1	0
Standard 45 deg Elbow	num_45deg_el	0.29	0	1	0
Butterfly Valve	numButfVlv	0.8	0	1	0
Gate Valve	numGtVlv	0.15	0	1	0
Angle Valve	numAngVlv	5	0	1	0
Globe Valve	numGlVlv	6.5	0	1	0
Duo Check Valve	numDuoChkVlv	0.8	0	1	0
Swing Check	numSwgChlVlv	1	0	1	0
Footvalve Standard	numFootStdVlv	1.4	0	1	0
Footvalve Poppet Type	numFootPopVlv	8	0	1	0
Tee Flow through	numTFlowHead	0.4	0	1	0
Tee Flow branch	numTFlowBran	1.1	0	1	0
Pipe exit	numPipExit	1	0	1	0
Pipe entrance	numPipEntr	0.8	0	1	0
Sudden contraction	numContraction	0	0	1	0
Sudden enlargement	numEnlarg	0	0	1	0
Strainer	numStrainer	8.43	0	1	0
User	User				0

				"K"Factor	0